## ReadMe
CK-A, the Analyst checkpoint: an auditable spreadsheet for a school's solar + battery (worked solution)
Energy Systems, Step by Step · Learn · built by scripts/build_learn_cka_sheet.py on 2026-11-06. Text CC BY 4.0, Honglin Li.
The case: Prairie Town High School (fictional) puts 250 kW-DC of rooftop solar and a 150 kW / 300 kWh battery behind its meter. Should the school district do it, and who pays and who benefits?
Deliver: (1) a boundary statement; (2) an assumptions log: every input with its value, unit, type, source and date, and a low and high value for the ones you test; (3) a model whose every number is a formula you can trace; (4) who pays and who benefits, with transfers kept apart from real costs; (5) a sensitivity of the main result.
Money: 2025 dollars, real (no inflation). Convert costs from other dollar years with the price index given in the log.
End value: the replacement battery (bought at the end of year 15, a 15-year life) has 5 of its 15 years left at year 25: count 5/15 of its cost as a residual value at year 25 (straight line).
Battery energy: about 200 equivalent full cycles a year, each taking in 300 kWh from the school's supply and returning 90%; the 10% lost is bought at the energy charge.
Rate reset: assume the utility recovers its whole remaining revenue shortfall from its other customers at the next rate reset.
Sheets: AssumptionsLog (inputs, sources, ranges) → Model (closed form, base and 16 scenario columns) → CashFlow (year by year, checks the Model) → WhoPays (parties, gross and net) → Sensitivity (sorted by swing).
Every number is a live formula; the cached values are what the course's test recomputes. Change an input in AssumptionsLog column C and the whole workbook follows.
Illustrative values are labelled as such in the log: they stand for numbers a real study would measure or take from the school's own bills and the utility's tariff sheet.

## AssumptionsLog
Assumptions log: every input, its type, its source and the range used in the sensitivity
Type: Sourced (a dated public document), Course data (from another Learn page's data), Illustrative (a stated choice for this case), Choice (a design decision), Derived (a formula on this sheet). All money in 2025 dollars unless the unit says otherwise.
ID | Input | Value | Unit | Type | Source (document, table, page) | As of | Note | Low | High
pvKW | Solar array size | 250 | kW-DC | Choice | EIA distributed-generation cost report (2024): https://www.eia.gov/analysis/studies/buildings/dg_storage_chp/pdf/dg_storage_chp.pdf | March 2024; read 6 Nov 2026 | The report's medium commercial rooftop system; the school roof is assumed to fit it.
pvCF | Solar capacity factor | 17.8% | fraction | Sourced | EIA distributed-generation cost report (2024): https://www.eia.gov/analysis/studies/buildings/dg_storage_chp/pdf/dg_storage_chp.pdf | March 2024; read 6 Nov 2026 | Table 2-5, 250 kW-DC, 2022, U.S. average; Kansas sun may differ. | 16.02% | 19.58%
self | Share of solar output used at the school | 75% | fraction | Illustrative | This case (stated choice) | 2026-11-06 | Summer break and weekends send the rest to the grid. | 60% | 90%
batKW | Battery power | 150 | kW | Choice | EIA distributed-generation cost report (2024): https://www.eia.gov/analysis/studies/buildings/dg_storage_chp/pdf/dg_storage_chp.pdf | March 2024; read 6 Nov 2026 | The report's medium commercial battery.
batKWh | Battery energy | 300 | kWh | Choice | EIA distributed-generation cost report (2024): https://www.eia.gov/analysis/studies/buildings/dg_storage_chp/pdf/dg_storage_chp.pdf | March 2024; read 6 Nov 2026 | Two hours at full power; the energy it takes in on each full cycle.
cut | Average cut in the monthly billed peak, share of battery power | 60% | fraction | Illustrative | This case (stated choice) | 2026-11-06 | A battery misses some peaks (forecast errors, long peaks, an empty battery). | 30% | 90%
cycles | Battery full cycles a year (each takes in 300 kWh) | 200 | per year | Illustrative | This case (stated choice) | 2026-11-06 | About one per school day. Equivalent full cycles: partial charges add up to whole ones. Each takes in 300 kWh and returns 90% of it; the 10% lost is bought at the energy charge.
rte | Battery round trip efficiency | 90% | fraction | Sourced | EIA distributed-generation cost report (2024): https://www.eia.gov/analysis/studies/buildings/dg_storage_chp/pdf/dg_storage_chp.pdf | March 2024; read 6 Nov 2026 | Table 3-3, 2022: the share of the energy put in that comes back out.
use | School electricity use | 1000000 | kWh a year | Illustrative | This case (stated choice) | 2026-11-06 | A large high school; not a measured building.
peak | School monthly billed peak | 400 | kW | Illustrative | This case (stated choice) | 2026-11-06 | Taken as the same every month.
price | Average commercial electricity price, Kansas | 0.1117 | $/kWh | Sourced | EIA Electric Power Monthly, Table 5.6.B: https://www.eia.gov/electricity/monthly/epm_table_grapher.php?t=epmt_5_6_b | issue of 23 Oct 2026 | January to August 2025; includes demand charges. The tariff below is set to give the school this average before the project. | 0.08936 | 0.13404
demand | Demand charge | 10 | $/kW-month | Illustrative | This case (stated choice) | 2026-11-06 | A two-part tariff; the energy charge is derived so the school's bill matches the EIA average. Its low and high re-derive the energy charge too, so the school's pre-project bill stays the same (a tariff rebalancing, not a dearer tariff). | 5 | 20
export | Credit for each kWh sent to the grid | 0.03 | $/kWh | Illustrative | This case (stated choice) | 2026-11-06 | Net billing near the utility's avoided energy cost (lesson A4).
capKW | Installed cost, solar + battery, per kW-DC of solar | 3170 | $/kW-DC (2022 $) | Sourced | EIA distributed-generation cost report (2024): https://www.eia.gov/analysis/studies/buildings/dg_storage_chp/pdf/dg_storage_chp.pdf | March 2024; read 6 Nov 2026 | Figure 3-5, 2022; read as per kW-DC of the solar array: 7% below the two systems' separate costs, as the report says co-location saves.
pvAloneKW | Installed cost, solar alone (check only) | 1903 | $/kW-DC (2022 $) | Sourced | EIA distributed-generation cost report (2024): https://www.eia.gov/analysis/studies/buildings/dg_storage_chp/pdf/dg_storage_chp.pdf | March 2024; read 6 Nov 2026 | Figure 2-4, 250 kW-DC, 2022; used only to check how Figure 3-5 is read.
batRepKW | Standalone battery cost, for the replacement | 2492 | $/kW (2022 $) | Sourced | EIA distributed-generation cost report (2024): https://www.eia.gov/analysis/studies/buildings/dg_storage_chp/pdf/dg_storage_chp.pdf | March 2024; read 6 Nov 2026 | Figure 3-4, 2022; held constant in real terms (no assumed cost change).
pvOM | Solar upkeep | 17.63 | $/kW-DC a year (2023 $) | Sourced | NLR ATB 2025, Commercial PV: https://atb.nlr.gov/electricity/2025/commercial_pv | read 6 Nov 2026 | ATB value for 2024, in 2023 dollars.
batOM | Battery upkeep | 63 | $/kW a year (2022 $) | Sourced | EIA distributed-generation cost report (2024): https://www.eia.gov/analysis/studies/buildings/dg_storage_chp/pdf/dg_storage_chp.pdf | March 2024; read 6 Nov 2026 | Figure 3-6, commercial, 2022.
i2022 | Price index, 2022 | 118.035 | index (2017 = 100) | Course data | EIA STEO Table 9a: https://www.eia.gov/outlooks/steo/ | October 2026 issue | The course's GDP price index (e0.json).
i2023 | Price index, 2023 | 122.389 | index (2017 = 100) | Course data | EIA STEO Table 9a: https://www.eia.gov/outlooks/steo/ | October 2026 issue | The course's GDP price index (e0.json).
i2025 | Price index, 2025 | 128.989 | index (2017 = 100) | Course data | EIA STEO Table 9a: https://www.eia.gov/outlooks/steo/ | October 2026 issue | The course's GDP price index (e0.json).
rate | Discount rate (real) | 4% | per year | Course data | This case (stated choice) | 2026-11-06 | The course's real rate (lessons 7 and 13, e0.json); a school district's own rate may differ. | 2% | 7%
years | Analysis period | 25 | years | Choice | This case (stated choice) | 2026-11-06 | A rooftop array's usual design life.
batLife | Battery useful life | 15 | years | Sourced | EIA distributed-generation cost report (2024): https://www.eia.gov/analysis/studies/buildings/dg_storage_chp/pdf/dg_storage_chp.pdf | March 2024; read 6 Nov 2026 | Table 3-3; replaced once, at the end of year 15.
avoidE | Utility's avoided energy cost | 0.03 | $/kWh | Illustrative | This case (stated choice) | 2026-11-06 | Taken equal to the export credit.
capCost | Utility's avoided capacity cost | 180 | $/kW a year | Course data | This case (stated choice) | 2026-11-06 | Lesson A4's illustrative $15 per kW-month for the town's tightest hour, times 12.
coinc | Share of the battery's peak cut that falls in the system's tightest hours | 50% | fraction | Illustrative | This case (stated choice) | 2026-11-06 | A school's peak need not be the grid's.
co2lb | Grid CO2 factor | 680 | lb per MWh | Sourced | EIA Kansas Electricity Profile 2024: https://www.eia.gov/electricity/state/kansas/ | data year 2024 | Kansas 2024 average of its power plants (location-based); a marginal factor would differ (lesson A10).
defl22 | 2022 dollars to 2025 dollars | 1.0928 | factor | Derived | This log | 2025 dollars | Index 2025 / index 2022.
defl23 | 2023 dollars to 2025 dollars | 1.0539 | factor | Derived | This log | 2025 dollars | Index 2025 / index 2023.
capital | Up-front cost, solar + battery | 866046.3634 | $ (2025) | Derived | This log | 2025 dollars | Installed cost per kW-DC x solar size x the 2022 factor. | 649534.7725 | 1082557.9542
repl | Battery replacement at the end of year 15 | 408489.7547 | $ (2025) | Derived | This log | 2025 dollars | Standalone cost x battery power x the 2022 factor.
omPV | Solar upkeep a year | 4645.1807 | $ (2025) | Derived | This log | 2025 dollars | Per kW-DC x solar size x the 2023 factor. | 3483.8855 | 5806.4758
omBat | Battery upkeep a year | 10326.9882 | $ (2025) | Derived | This log | 2025 dollars | Per kW x battery power x the 2022 factor. | 7745.2411 | 12908.7352
co2 | Grid CO2 factor in metric tonnes | 0.30844 | t per MWh | Derived | This log | 2025 dollars | lb per MWh x 0.45359237 kg per lb / 1,000.
coloc | Check: saving from installing together | 6.715% | fraction | Derived | This log | 2025 dollars | 1 - combined cost / (solar alone + standalone battery), 2022 dollars: positive, as the report says co-location saves.

## Model
Model: the school's solar + battery in closed form, one column per scenario
Column C is the base case. Each other column changes one input (the one in its heading) to its low or high value from AssumptionsLog; every other cell is the same formula, filled right.
Quantity | Unit | Base | Up-front cost, low | Up-front cost, high | Demand charge (pre-project bill held), low | Demand charge (pre-project bill held), high | Average electricity price, low | Average electricity price, high | Discount rate, low | Discount rate, high | Solar capacity factor, low | Solar capacity factor, high | Share used at the school, low | Share used at the school, high | Battery's cut in the billed peak, low | Battery's cut in the billed peak, high | Upkeep, solar and battery, low | Upkeep, solar and battery, high
Solar array size | kW-DC | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
Solar capacity factor | fraction | 17.8% | 17.8% | 17.8% | 17.8% | 17.8% | 17.8% | 17.8% | 17.8% | 17.8% | 16.02% | 19.58% | 17.8% | 17.8% | 17.8% | 17.8% | 17.8% | 17.8%
Share of solar output used at the school | fraction | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 60% | 90% | 75% | 75% | 75% | 75%
Battery power | kW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
Battery energy | kWh | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
Average cut in the monthly billed peak, share of battery power | fraction | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 30% | 90% | 60% | 60%
Battery full cycles a year (each takes in 300 kWh) | per year | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
Battery round trip efficiency | fraction | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90%
School electricity use | kWh a year | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000
School monthly billed peak | kW | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
Average commercial electricity price, Kansas | $/kWh | 0.1117 | 0.1117 | 0.1117 | 0.1117 | 0.1117 | 0.08936 | 0.13404 | 0.1117 | 0.1117 | 0.1117 | 0.1117 | 0.1117 | 0.1117 | 0.1117 | 0.1117 | 0.1117 | 0.1117
Demand charge | $/kW-month | 10 | 10 | 10 | 5 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Credit for each kWh sent to the grid | $/kWh | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Up-front cost, solar + battery | $ (2025) | 866046.3634 | 649534.7725 | 1082557.9542 | 866046.3634 | 866046.3634 | 866046.3634 | 866046.3634 | 866046.3634 | 866046.3634 | 866046.3634 | 866046.3634 | 866046.3634 | 866046.3634 | 866046.3634 | 866046.3634 | 866046.3634 | 866046.3634
Battery replacement at the end of year 15 | $ (2025) | 408489.7547 | 408489.7547 | 408489.7547 | 408489.7547 | 408489.7547 | 408489.7547 | 408489.7547 | 408489.7547 | 408489.7547 | 408489.7547 | 408489.7547 | 408489.7547 | 408489.7547 | 408489.7547 | 408489.7547 | 408489.7547 | 408489.7547
Solar upkeep a year | $ (2025) | 4645.1807 | 4645.1807 | 4645.1807 | 4645.1807 | 4645.1807 | 4645.1807 | 4645.1807 | 4645.1807 | 4645.1807 | 4645.1807 | 4645.1807 | 4645.1807 | 4645.1807 | 4645.1807 | 4645.1807 | 3483.8855 | 5806.4758
Battery upkeep a year | $ (2025) | 10326.9882 | 10326.9882 | 10326.9882 | 10326.9882 | 10326.9882 | 10326.9882 | 10326.9882 | 10326.9882 | 10326.9882 | 10326.9882 | 10326.9882 | 10326.9882 | 10326.9882 | 10326.9882 | 10326.9882 | 7745.2411 | 12908.7352
Discount rate (real) | per year | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 2% | 7% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4%
Analysis period | years | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Battery useful life | years | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Utility's avoided energy cost | $/kWh | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Utility's avoided capacity cost | $/kW a year | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
Share of the battery's peak cut that falls in the system's tightest hours | fraction | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50%
Calculations
Energy charge (derived: the school's bill before the project matches the EIA average) | $/kWh | 0.0637 | 0.0637 | 0.0637 | 0.0877 | 0.0157 | 0.04136 | 0.08604 | 0.0637 | 0.0637 | 0.0637 | 0.0637 | 0.0637 | 0.0637 | 0.0637 | 0.0637 | 0.0637 | 0.0637
Solar output | kWh a year | 389820 | 389820 | 389820 | 389820 | 389820 | 389820 | 389820 | 389820 | 389820 | 350838 | 428802 | 389820 | 389820 | 389820 | 389820 | 389820 | 389820
Used at the school | kWh a year | 292365 | 292365 | 292365 | 292365 | 292365 | 292365 | 292365 | 292365 | 292365 | 263128.5 | 321601.5 | 233892 | 350838 | 292365 | 292365 | 292365 | 292365
Sent to the grid | kWh a year | 97455 | 97455 | 97455 | 97455 | 97455 | 97455 | 97455 | 97455 | 97455 | 87709.5 | 107200.5 | 155928 | 38982 | 97455 | 97455 | 97455 | 97455
Saving on energy charges | $ a year | 18623.6505 | 18623.6505 | 18623.6505 | 25640.4105 | 4590.1305 | 12092.2164 | 25155.0846 | 18623.6505 | 18623.6505 | 16761.2855 | 20486.0156 | 14898.9204 | 22348.3806 | 18623.6505 | 18623.6505 | 18623.6505 | 18623.6505
Credit for exports | $ a year | 2923.65 | 2923.65 | 2923.65 | 2923.65 | 2923.65 | 2923.65 | 2923.65 | 2923.65 | 2923.65 | 2631.285 | 3216.015 | 4677.84 | 1169.46 | 2923.65 | 2923.65 | 2923.65 | 2923.65
Saving on demand charges | $ a year | 10800 | 10800 | 10800 | 5400 | 21600 | 10800 | 10800 | 10800 | 10800 | 10800 | 10800 | 10800 | 10800 | 5400 | 16200 | 10800 | 10800
Battery losses | kWh a year | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
Cost of battery losses | $ a year | -382.2 | -382.2 | -382.2 | -526.2 | -94.2 | -248.16 | -516.24 | -382.2 | -382.2 | -382.2 | -382.2 | -382.2 | -382.2 | -382.2 | -382.2 | -382.2 | -382.2
Bill saving, gross | $ a year | 31965.1005 | 31965.1005 | 31965.1005 | 33437.8605 | 29019.5805 | 25567.7064 | 38362.4946 | 31965.1005 | 31965.1005 | 29810.3705 | 34119.8306 | 29994.5604 | 33935.6406 | 26565.1005 | 37365.1005 | 31965.1005 | 31965.1005
Upkeep, solar and battery | $ a year | 14972.1689 | 14972.1689 | 14972.1689 | 14972.1689 | 14972.1689 | 14972.1689 | 14972.1689 | 14972.1689 | 14972.1689 | 14972.1689 | 14972.1689 | 14972.1689 | 14972.1689 | 14972.1689 | 14972.1689 | 11229.1266 | 18715.2111
Net saving a year | $ a year | 16992.9316 | 16992.9316 | 16992.9316 | 18465.6916 | 14047.4116 | 10595.5375 | 23390.3257 | 16992.9316 | 16992.9316 | 14838.2016 | 19147.6617 | 15022.3915 | 18963.4717 | 11592.9316 | 22392.9316 | 20735.9739 | 13249.8894
Annuity factor | years | 15.6221 | 15.6221 | 15.6221 | 15.6221 | 15.6221 | 15.6221 | 15.6221 | 19.5235 | 11.6536 | 15.6221 | 15.6221 | 15.6221 | 15.6221 | 15.6221 | 15.6221 | 15.6221 | 15.6221
Present value of net savings | $ | 265464.9366 | 265464.9366 | 265464.9366 | 288472.5111 | 219449.7877 | 165524.3346 | 365405.5387 | 331760.7613 | 198028.5424 | 231803.5715 | 299126.3017 | 234681.0017 | 296248.8716 | 181105.7049 | 349824.1683 | 323939.0413 | 206990.8319
Present value of the battery replacement | $ | 226819.8605 | 226819.8605 | 226819.8605 | 226819.8605 | 226819.8605 | 226819.8605 | 226819.8605 | 303513.9048 | 148055.4857 | 226819.8605 | 226819.8605 | 226819.8605 | 226819.8605 | 226819.8605 | 226819.8605 | 226819.8605 | 226819.8605
Replacement battery's value left at the end (straight line: 5 of its 15 years left at year 25) | $ | 136163.2516 | 136163.2516 | 136163.2516 | 136163.2516 | 136163.2516 | 136163.2516 | 136163.2516 | 136163.2516 | 136163.2516 | 136163.2516 | 136163.2516 | 136163.2516 | 136163.2516 | 136163.2516 | 136163.2516 | 136163.2516 | 136163.2516
Present value of that residual | $ | 51077.1235 | 51077.1235 | 51077.1235 | 51077.1235 | 51077.1235 | 51077.1235 | 51077.1235 | 82995.7053 | 25087.9671 | 51077.1235 | 51077.1235 | 51077.1235 | 51077.1235 | 51077.1235 | 51077.1235 | 51077.1235 | 51077.1235
MAIN RESULT: net present value to the school | $ | -776324.1637 | -559812.5729 | -992835.7546 | -753316.5893 | -822339.3127 | -876264.7658 | -676383.5617 | -754803.8016 | -790985.3396 | -809985.5288 | -742662.7986 | -807108.0987 | -745540.2288 | -860683.3954 | -691964.9321 | -717850.059 | -834798.2684
Utility's avoided cost | $ a year | 19614.6 | 19614.6 | 19614.6 | 19614.6 | 19614.6 | 19614.6 | 19614.6 | 19614.6 | 19614.6 | 18445.14 | 20784.06 | 19614.6 | 19614.6 | 15564.6 | 23664.6 | 19614.6 | 19614.6
Cost shift to the utility's other customers | $ a year | 12350.5005 | 12350.5005 | 12350.5005 | 13823.2605 | 9404.9805 | 5953.1064 | 18747.8946 | 12350.5005 | 12350.5005 | 11365.2305 | 13335.7706 | 10379.9604 | 14321.0406 | 11000.5005 | 13700.5005 | 12350.5005 | 12350.5005
Net present value to the other customers | $ | -192940.5062 | -192940.5062 | -192940.5062 | -215948.0806 | -146925.3572 | -92999.9041 | -292881.1082 | -241124.4589 | -143927.5849 | -177548.5387 | -208332.4736 | -162156.5712 | -223724.4411 | -171850.6982 | -214030.3141 | -192940.5062 | -192940.5062
Net present value, resource view (all parties) | $ | -969264.6699 | -752753.0791 | -1185776.2607 | -969264.6699 | -969264.6699 | -969264.6699 | -969264.6699 | -995928.2605 | -934912.9244 | -987534.0675 | -950995.2723 | -969264.6699 | -969264.6699 | -1032534.0937 | -905995.2461 | -910790.5652 | -1027738.7746
Check: school + other customers - resource view (should be 0) | $ | 1.1642e-10 | 1.1642e-10 | 2.3283e-10 | 2.3283e-10 | 2.3283e-10 | 1.1642e-10 | 2.3283e-10 | 0 | -1.1642e-10 | 0 | 2.3283e-10 | 2.3283e-10 | 1.1642e-10 | 0 | 2.3283e-10 | 1.1642e-10 | 1.1642e-10

## CashFlow
Cash flow, base case, year by year (2025 dollars, real)
Checks the Model's closed form: the sum of present values equals Model!C46.
Year | Capital and replacement | Bill saving | Upkeep | Residual value | Net cash flow | Discount factor | Present value | Cumulative cash (not discounted)
0 | -866046.3634 | 0 | 0 | 0 | -866046.3634 | 1 | -866046.3634 | -866046.3634
1 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.96154 | 16339.3574 | -849053.4317
2 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.92456 | 15710.9205 | -832060.5001
3 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.889 | 15106.6544 | -815067.5684
4 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.8548 | 14525.6292 | -798074.6368
5 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.82193 | 13966.9511 | -781081.7051
6 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.79031 | 13429.7607 | -764088.7735
7 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.75992 | 12913.2315 | -747095.8419
8 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.73069 | 12416.5687 | -730102.9102
9 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.70259 | 11939.0084 | -713109.9786
10 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.67556 | 11479.8157 | -696117.0469
11 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.64958 | 11038.2844 | -679124.1153
12 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.6246 | 10613.735 | -662131.1836
13 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.60057 | 10205.5144 | -645138.252
14 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.57748 | 9812.9946 | -628145.3203
15 | -408489.7547 | 31965.1005 | -14972.1689 | 0 | -391496.8231 | 0.55526 | -217384.2888 | -1019642.1434
16 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.53391 | 9072.6651 | -1002649.2118
17 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.51337 | 8723.7165 | -985656.2801
18 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.49363 | 8388.1889 | -968663.3485
19 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.47464 | 8065.5663 | -951670.4169
20 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.45639 | 7755.3522 | -934677.4852
21 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.43883 | 7457.0694 | -917684.5536
22 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.42196 | 7170.259 | -900691.6219
23 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.40573 | 6894.4798 | -883698.6903
24 | 0 | 31965.1005 | -14972.1689 | 0 | 16992.9316 | 0.39012 | 6629.3075 | -866705.7586
25 | 0 | 31965.1005 | -14972.1689 | 136163.2516 | 153156.1832 | 0.37512 | 57451.4577 | -713549.5754
Total present value | [6 empty] | -776324.1637
Check: total minus the Model's closed form (should be 0) | [6 empty] | -1.1642e-10
Lowest cumulative cash in 25 years | [6 empty] | -1019642.1434

## WhoPays
Who pays and who benefits (screening estimates, 2025 dollars)
Each party's money, with transfers kept apart from real costs. The parties add up to the resource view: a transfer is one party's gain and another's loss.
Party | A year | Present value | What it is
The school district (its budget and taxpayers) | 16992.9316 | -776324.1637 | Pays the capital, upkeep and replacement; gets the gross bill saving.
The utility's other customers (once rates are reset) | -12350.5005 | -192940.5062 | The part of the school's bill saving the utility does not save in costs: a transfer, recovered from the others at the next rate reset, as the brief assumes (until then, and without that assumption, it stays with the utility).
Federal taxpayers | 0 | 0 | No tax credit is counted (boundary). Tax-exempt and governmental entities can benefit from certain clean-energy credits through elective pay (IRS, reviewed 27 Jun 2026); if counted, it is a transfer from federal taxpayers to the school, not a lower resource cost.
Sum of the parties |  | -969264.6699
Resource view (Model) |  | -969264.6699
Check: sum of the parties minus the resource view (should be 0) |  | 1.1642e-10
Gross against net, a year
The school's gross bill saving | 31965.1005
of which a real cost saving (the utility's avoided cost) | 19614.6
of which a transfer from the other customers | 12350.5005
Not in money (stated, not valued)
CO2 avoided, tonnes a year (location-based average factor) | 118.3865 |  | An average factor answers an inventory question; the change the project causes needs a marginal or consequential estimate (lesson A10).
Resilience: backup power in an outage |  |  | Not counted: the system as costed has no islanding switch or critical-load panel.
Jobs: installation work |  |  | Installation is job-years (temporary work), not permanent jobs; not estimated here (no sourced coefficient).

## Sensitivity
Sensitivity of the main result: one input at a time
Each row reads the Model's scenario columns. Rows are sorted by swing (largest first).
Input | Low value | High value | NPV at low | NPV at high | Swing
Up-front cost | 649534.7725 | 1082557.9542 | -559812.5729 | -992835.7546 | 433023.1817
Average electricity price | 0.08936 | 0.13404 | -876264.7658 | -676383.5617 | 199881.2041
Battery's cut in the billed peak | 30% | 90% | -860683.3954 | -691964.9321 | 168718.4634
Upkeep, solar and battery ($ a year) | 11229.1266 | 18715.2111 | -717850.059 | -834798.2684 | 116948.2094
Demand charge (pre-project bill held) | 5 | 20 | -753316.5893 | -822339.3127 | 69022.7234
Solar capacity factor | 16.02% | 19.58% | -809985.5288 | -742662.7986 | 67322.7302
Share used at the school | 60% | 90% | -807108.0987 | -745540.2288 | 61567.8699
Discount rate | 2% | 7% | -754803.8016 | -790985.3396 | 36181.538
Base NPV |  |  | -776324.1637
Lowest and highest NPV in any one swing |  |  | -992835.7546 | -559812.5729